| Hazards | Is the hazard present? Y/N | What is the risk? | Risk rating H = High M = Medium L = Low | Control measures | Is this control in place? Y/N | If no, what actions are required to implement the control? | Person responsible | Date action completed |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Legionella bacteria |  | Pontiac fever Legionnaires disease (potentially fatal form of pneumonia) | H | Competent person with relevant skills, knowledge and experience identified to conduct site specific risk assessment |  |  |  |  |
|  |  |  | H | Sources of possible risk of Legionella identified from work activities and water systems at the workplace. To consider: - Potential for Legionella growth e.g. water stagnation, sources of contamination etc. - Potential for aerosol generation - Presence of susceptible persons - Adequacy of existing site management records and arrangements - Efficacy of existing preventative and control measures - Systems at greatest risk assessed, e.g. showers, cisterns, lawn sprinklers, firefighting systems – sprinklers or hoses, humidifiers in food cabinets, spray washing equipment, emergency showers, eye wash stations, etc |  |  |  |  |
|  |  |  | H | Documented Procedure(s)/Written Scheme in place to prevent and control risk from Legionella (Legionella control plan) The Legionella Control plan contains: - Description of the water system and the safe and correct operation of the system and any relevant plant and equipment - An up to date schematic diagram of the system - Details of the tests and checks, e.g. temperature measurements, to be carried out, by whom and when and what records are kept and by whom - Details of the remedial action to be taken if the system is out of specification Systems are in place for change control– i.e. updating the schematic diagrams if changes are made The cold water tank is fitted with a cover and insect screen(s) and located in a cool place and protected from extremes of temperature |  |  |  |  |

| Hazards | Is the hazard present? Y/N | What is the risk? | Risk rating H = High M = Medium L = Low | Control measures | Is this control in place? Y/N | If no, what actions are required to implement the control? | Person responsible | Date action completed |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Legionella bacteria |  | Pontiac fever Legionnaires disease (potentially fatal form of pneumonia) |  | Cold water pipework insulated and kept away from heat sources Cold water storage holds enough for a day’s use only and has no build-up of scale or sludge Hot water distribution pipes insulated Biocide treatments used for cooling towers Hot water stored above 60°C and distributed at above 50°C. Cold water kept below 20°C and checks recorded Water storage tanks are checked and cleaned, any build up of sludge/slime is cleaned, and tanks are disinfected annually Records of flushing and purging are kept Shower heads cleaned, descaled and disinfected quarterly in accordance with documented procedures and records kept There are arrangements in place for little used outlets, to either: - flush through showers/ taps/emergency showers and all other sources arising on at least a weekly basis, or - carry out a safe purge of the water system before use e.g. prior to reopening after summer holidays |  |  |  |  |
|  |  |  | H | Competent ‘Responsible person’ and deputy identified to oversee the Legionella control plan Relevant staff have been provided with instruction and training on legionella control |  |  |  |  |

| Hazards | Is the hazard present? Y/N | What is the risk? | Risk rating H = High M = Medium L = Low | Control measures | Is this control in place? Y/N | If no, what actions are required to implement the control? | Person responsible | Date action completed |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Legionella bacteria |  | Pontiac fever Legionnaires disease (potentially fatal form of pneumonia) | H | Records kept of all checks and tests and reviewed to ensure Legionella control plan is effective All test and inspection records are kept for 5 years |  |  |  |  |

If there is one or more High Risk (H) actions needed, then the risk of injury could be high and immediate action should be taken.

Medium Risk (M) actions should be dealt with as soon as possible.   Low Risk (L) actions should be dealt with as soon as practicable.

Risk Assessment carried out by: 		Date:	/	/

© All Rights Reserved

Reference

For further information and guidance on Legionella - refer to the ‘National Guidelines for the Control of Legionellosis in Ireland, 2009 - published by the Health Protection Surveillance 
Centre web site; http://www.hpsc.ie/hpsc/A-Z/Respiratory/Legionellosis/Publications